Drinking Water Quality and Compliance

Town Short Form – A Template for Annual Notice to Consumers

(Note:  This short form may be used for communities or waterworks serving a population of less than 5000).

Introduction

Saskatchewan Ministry of Environment requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Minister’s Order or Permit to Operate a waterworks.  The following is a summary of the Town of Cabri water quality and sample submission compliance record for the January 1 to December 31, 2017 time period.  This report was completed on June 12, 2018.  Readers should refer to Environment’s Municipal Drinking Water Quality Monitoring Guidelines, November 2002, EPB 202 for more information on minimum sample submission requirements and the meaning of type of sample.  Permit requirements for a specific waterworks may require more sampling than outlined in the department’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of Selenium in a water supply”, more detailed information is available from:  http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html .

## Water Quality Standards

# Bacteriological Quality

Regular Samples	Regular Samples	  # of Positive Regular

Parameter/Location	Limit			Required		Submitted	  Submitted (%)

Total Coliform and	0 Organisms/100 mL	52		51		0

E. coli			0 Organisms/100mL	52		51		0

Background Bacteria	Less than 200/100 mL	52		51		0

Water Disinfection –

Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples

Minimum	Total Chlorine	Free Chlorine	# Tests	# Tests	# Adequate

Parameter	Limit	Residual Range	Residual Range	Required	Submitted	Chlorine (%)

Chlorine	0.1 mg/L free OR

Residual	0.5 mg/L total	0.5-2.88	0.1-2.10	52	51		100%

Water Disinfection - Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records

Test Level	# Tests                # Tests Not Meeting

Parameter	Limit (mg/L)	Range	Performed          Requirements

Free Chlorine Residual	at least 0.7	0.70-4.14	366                   0

A minimum of 0.7 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.7 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Parameter	Limit	Test Level	# Tests Not Meeting	Maximum	# Tests           # Tests		# Tests

(NTU) 	Range	Requirements	Turbidity (NTU)	Required        Performed	Performed

Turbidity	0.3	0.017-0.199	0	0.199	366                 366

Chemical – Health Category

All waterworks serving less than 5000 persons are required to submit water samples for SE’s Chemical Health category once every 2 years.  The Chemical Health category includes analysis for arsenic, barium, boron, cadmium, chromium, fluoride, lead, nitrate, selenium and uranium.

The last sample for Chemical Health analysis was submitted on May 15, 2017.  Sample results indicated that the provincial drinking water quality standards were not exceeded.

Limit	Limit	Sample	# Samples

Parameter	MAC(mg/L)	IMAC (mg/L)	Result(s)	Exceeding Limit

Arsenic	0.010		0.40ug/L	0_______________   * Results expressed

Barium	1.0		34ug/L	0_______________ 	  as average values

Boron		5.0	0.1mg/L	0_______________      for communities or

Cadmium	0.005		<0.15ug/L	0_______________      waterworks that

Chromium	0.05		1.3ug/L	0_______________      fluoridate drinking

Fluoride (avg*)	1.5		0.05mg/L	0_______________      water supplies or

Lead	0.01		0.30ug/L	0_______________      those with elevated

Nitrate (avg.*)	45.0		0.04mg/L	0_______________      concentrations of

Seleniuum	0.01		<1.13ug/L	0_______________      fluoride or nitrates.

Uranium	0.02		0.30ug/L	0_______________

Chemical – Trihalomethanes (THMs)

Parameter	THMs		Sample	# Samples	#  Samples

Limit (mg/L)		Result (average) 	Required	Submitted

Trihalomethanes	0.1	0.016                       4 (1 every 3 months)	4

Haloacetic Acids	0.08                      0.016                       4 (1 every 3 months)          4

Note:  Only water supplies derived from surface water or groundwater under the influence of surface water are required to monitor for THMs.  Waterworks using groundwater sources beyond the influence of surface water do not need to report THMs since sampling/analysis will not likely have been performed.

More information on water quality and sample submission performance may be obtained from:

Town of Cabri

Box 200

Cabri, SK S0N 0J0

306-587-2500

townofcabri@sasktel.net

June 2015 EPB 536D