Drinking Water Quality and Compliance

Town of Cabri - Annual Notice to Consumers

(Note:  This short form may be used for communities or waterworks serving a population of less than 5000).

Introduction

The Water Security Agency and the Ministry of Environment requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Minister’s Order or Permit to Operate a waterworks.  The following is a summary of the Town of Cabri’s water quality and sample submission compliance record for the January 1 to December 31, 2023 time period.  This report was completed on May 29, 2024 (must be completed before June 30 each year on a calendar year based reporting frequency).  Readers should refer to Water Security Agency’s Municipal Drinking Water Quality Monitoring Guidelines, June 2015, EPB 502 for more information on minimum sample submission requirements and the meaning of type of sample.  Permit requirements for a specific waterworks may require more sampling than outlined in the department’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of Selenium in a water supply”, more detailed information is available from:  http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html .

## Water Quality Standards

# Bacteriological Quality

Regular Samples	Regular Samples	  # of Positive Regular

Parameter/Location	Limit			Required		Submitted	  Submitted (%)

Total Coliform 		0 Organisms/100 mL	52		52		0

E. coli			0 Organisms/100 mL	52		52		0

Background Bacteria	Less than 200/100 mL	52		52		0

Water Disinfection –

Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples

Minimum	Total Chlorine	Free Chlorine	# Tests	# Tests	# Adequate

Parameter	Limit	Residual Range	Residual Range	Required	Submitted	Chlorine (%)

Chlorine	0.1 mg/L free OR

Residual	0.5 mg/L total	0.59-4.61	0.14-3.32	52	52		100%

Water Disinfection - Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records

Test Level	# Tests                # Tests Not Meeting

Parameter	Limit (mg/L)	Range	Performed          Requirements

Free Chlorine Residual	at least 0.50	0.61-3.82	365                   0

A minimum of 0.50 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.50 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Parameter	Limit	Test Level	# Tests Not Meeting	Maximum	# Tests           # Tests		# Tests

(NTU) 	Range	Requirements	Turbidity (NTU)	Required        Performed	Performed

Turbidity	0.3	0.024-0.125         0	0.125	365                  365	____________

Chemical – Health Category

All waterworks serving less than 5000 persons are required to submit water samples for SE’s Chemical Health category once every 2 years.  The Chemical Health category includes analysis for arsenic, barium, boron, cadmium, chromium, fluoride, lead, nitrate, selenium and uranium. *TESTS PERFORMED IN 2023 AS PER REGULATIONS.

The last sample for Chemical Health analysis was submitted on February 6, 2023

Sample results indicated that the provincial drinking water quality standards were not exceeded.

Limit	Limit	Sample	# Samples

Parameter	MAC(mg/L)	IMAC (mg/L)	Result(s)	Exceeding Limit

Arsenic	0.010		1.0ug/L	_0_____________   * Results expressed

Barium	1.0		56.2 ug/L	_0_____________ 	as average values

Boron		5.0	0.2 mg/L	_0_____________      for communities or

waterworks that

Cadmium	0.005		<0.15 ug/L	_0_____________      fluoridate drinking

those with elevated

Chromium	0.05		0.70 ug/L	_0_____________      concentrations of

Fluoride (avg*)	1.5		0.07 mg/L	_0_____________      fluoride or nitrates.

Lead	0.01		0.10 ug/L	_0_____________

Nitrate (avg.*)	45.0		0.90 mg/L	_0_____________

Seleniuum	0.01		<1.13 ug/L	_0_____________

Uranium	0.02		<0.11 ug/L	_0_____________

Chemical – Trihalomethanes (THMs)and Haloacetic Acids (HAAs)

Parameter	THMs		Sample	# Samples	#  Samples

Limit (mg/L)		Result (average) 	Required	Submitted

Trihalomethanes	0.1	0.0231                    4 (1 every 3 months)	4

Haloacetic Acids	    0.08		    0.0332                   4 (1 every 3 months)	       4

Note:  Only water supplies derived from surface water or groundwater under the influence of surface water are required to monitor for THMs and HAAs.  Waterworks using groundwater sources beyond the influence of surface water do not need to report THMs or HAAs since sampling/analysis will not likely have been performed unless otherwise noted in the waterworks permit to operate

# General Chemical

Aesthetic 		Sample Results	# Samples  # Samples

### Parameter	Objectives * (mg/L)	(average)	Required     Submitted

Alkalinity	500	76.8 mg/l	4		1

Bicarbonate	No Objective	94.0 mg/l	4	1

Calcium	No Objective	136.0 mg/l	4	1

Carbonate	No Objective	0		4	1

Chloride	250	44.2 mg/l	4	1

Conductivity	No Objective	1779 uS/cm	4	1

Hardness	800	718.0 mg/l	4		1

Magnesium	200	92.0 mg/l	4		1

PH	No Objective	6.8 pH units		4	1

Sodium	300	178.0 mg/l		4	1

Sulphate	500	852.4 mg/l	 	4	1

Total dissolved

Solids                   1500	                         1416 mg/l 	4	1

All waterworks serving less than 5000 persons are required to submit water samples for SE’s General Chemical category once every two years if a ground water source and once per three months every second year if a surface water or blended surface/groundwater source.  The General Chemical category includes analysis for alkalinity, bicarbonate, calcium, carbonate, chloride, conductivity, hardness (as CaCO3), magnesium, sodium, sulphate and total dissolved solids.

The last sets of quarterly samples for General Chemical analysis are required in 2023 and were submitted on February 6, 2023.  Sample results indicated that there were no exceedences of the provincial aesthetic objectives for the General Chemical category.

*Objectives apply to certain characteristics of or substances found in water for human consumptive or hygienic use.  The presence of these substances will affect the acceptance of water by consumers and/or interfere with the practice of supplying good quality water.  Compliance with drinking water aesthetic objectives is not mandatory as these objectives are in the range where they do not constitute a health hazards.  The aesthetic objectives for several parameters (including hardness as CaCO3, magnesium, sodium and total dissolved solids) consider regional differences in drinking water sources and quality.

More information on water quality and sample submission performance may be obtained from:

Town of Cabri

Box 200

Cabri, SK S0N 0J0

306-587-2500

townofcabri@sasktel.net

June 2015         EPB 536D